## Generator Details
Parameter | Value
Minimum fault level (MVA) | 920
Maximum fault level (MVA) | 2150
Minimum SCR | 3.68
Minimum SCR X2R | 5
Maximum SCR | 8.6
Maximum SCR X2R | 6.5
POC Qmax (MVAr) | 98.75
POC Qmin (MVAr) | -98.75
POC Qbase (MVAr) | 98.75
POC Pbase (MW) | 250
POC Pmax (MW) | 250
POC Pmin (MW) | 0
POC Sbase (MVA) | 268.7965
Voltage droop (%) | 3.95%
Normal Vpoc (pu) | 1.06
Vqmin (pu) | 1.0995
Vqmax (pu) | 1.0205
POC Vbase (kV) | 220

## FlatRun
Deliverable | Category | Figure Number | Clause | Test No | Subtest No | File_Name | Steps_Per_Write | PSSE | PSCAD | Grid_SCR | Grid_FL_MVA_sig | Grid_X2R_sig | Vpoc_pu_sig | Qpoc_pu | Qpoc_MVAr_sig | Vref_init | Ppoc_pu | Ppoc_MW_sig | PSSE Commands | Post_Init_Duration_s | Model_Relpath | Vpoc_disturbance_pu_sig | U_Ov
CSR | FlatRun | 1 |  | 1 |  | CSR_FlatRun_001 | 10000 | TRUE | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | 2

## Branch_Trips_SH
Deliverable | Category | Model Name | Test No | Subtest No | Case | File_Name | Steps_Per_Write | PSSE | PSCAD | NEAR | FAR | CB FAIL | CB FAIL SCENARIO | RECLOSE | Fault_Type_sig | Fault_Time_sig | Fault_Duration_sig | Ures_sig | Zf2Zs_sig | Rf_Offset_sig | Xf_Offset_sig | Fault_X2R_sig | Distance | Generator Connected | Generator Disconnected | Fault_Timing_Signal_sig | PSSE Commands | Post_Init_Duration_s | Vslack_pu_sig | Model_Relpath | Original | Comment | Schemes | Schemes2 | Schemes3
CSR | Balanced Faults | SummerHigh | 1 |  | SummerHigh | SummerHigh_001 | 100 | TRUE | TRUE | 0.43 | 0.12 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.43s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 2 |  | SummerHigh | SummerHigh_002 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'SHTS220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'SHTS220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 3 |  | SummerHigh | SummerHigh_003 | 100 | TRUE | TRUE | 0.43 | 0.12 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.43s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 4 |  | SummerHigh | SummerHigh_004 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'DED220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'DED220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 5 |  | SummerHigh | SummerHigh_005 | 100 | TRUE | TRUE | 0.08 | 0.1 | 0.175 | FALSE | 3 | 7 | 5 | 0.1 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.1s ↓ 0 | TRIP BRANCH 'HZ500_SM500¦NEAR' AT 5.08s; TRIP BRANCH 'HZ500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'HZ500_SM500¦NEAR' AT 8.08s; RESTORE BRANCH 'HZ500_SM500¦FAR' AT 8.08s; APPLY FAULT TO BRANCH 'HZ500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.08s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 6 |  | SummerHigh | SummerHigh_006 | 100 | TRUE | TRUE | 0.175 | 0.175 | 0.175 | TRUE | 3 | 7 | 5 | 0.175 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.175s ↓ 0 | TRIP BRANCH 'RO500_SM500¦NEAR' AT 5.175s; TRIP BRANCH 'RO500_SM500¦FAR' AT 5.175s; APPLY FAULT TO BRANCH 'RO500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.175s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.175s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.175s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.175s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 7 |  | SummerHigh | SummerHigh_007 | 100 | TRUE | TRUE | 0.8 | 0.1 | 0.175 | FALSE | 3 | 7 | 5 | 0.8 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.8s ↓ 0 | TRIP BRANCH 'KE500_SM500¦NEAR' AT 5.8s; TRIP BRANCH 'KE500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'KE500_SM500¦NEAR' AT 8.8s; RESTORE BRANCH 'KE500_SM500¦FAR' AT 8.8s; APPLY FAULT TO BRANCH 'KE500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.8s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 8 |  | SummerHigh | SummerHigh_008 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 9 |  | SummerHigh | SummerHigh_009 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'DE330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'DE330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=7, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 10 |  | SummerHigh | SummerHigh_010 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'JIN330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'JIN330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'JIN330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'JIN330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'JIN330_WO330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 11 |  | SummerHigh | SummerHigh_011 | 100 | TRUE | TRUE | 0.25 | 0.25 | 0.25 | TRUE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'DED330_MUR330¦NEAR' AT 5.25s; TRIP BRANCH 'DED330_MUR330¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'DED330_MUR330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.01 | Not active for this case P<400 MW (pickup is 1260 MW) | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦FAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦NEAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦FAR' AT 15s
CSR | Balanced Faults | SummerHigh | 12 |  | SummerHigh | SummerHigh_012 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_SM330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_SM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_SM330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 13 |  | SummerHigh | SummerHigh_013 | 100 | TRUE | TRUE | 0.25 | 0.25 | 0.25 | TRUE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'LWTM330_MUR330¦NEAR' AT 5.25s; TRIP BRANCH 'LWTM330_MUR330¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'LWTM330_MUR330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 14 |  | SummerHigh | SummerHigh_014 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_UPTM330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_UPTM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_UPTM330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 15 |  | SummerHigh | SummerHigh_015 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GLEN220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GLEN220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 16 |  | SummerHigh | SummerHigh_016 | 100 | TRUE | TRUE | 0.43 | 0.43 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHEP220_GLEN220¦NEAR' AT 5.43s; TRIP BRANCH 'SHEP220_GLEN220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'SHEP220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 17 |  | SummerHigh | SummerHigh_017 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHEP220_GLEN220¦NEAR' AT 5.12s; TRIP BRANCH 'SHEP220_GLEN220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'SHEP220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 18 |  | SummerHigh | SummerHigh_018 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_MTB220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_MTB220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_MTB220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 19 |  | SummerHigh | SummerHigh_019 | 100 | TRUE | TRUE | 0.43 | 0.43 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'FO220_SHEP220¦NEAR' AT 5.43s; TRIP BRANCH 'FO220_SHEP220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'FO220_SHEP220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 20 |  | SummerHigh | SummerHigh_020 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01; TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; TRIP BRANCH 'MURRA_MRTS' AT 5.18s; TRIP BRANCH 'MURRA_KIAM' AT 5.18s; TRIP MACHINE 'BULGG1' AT 5.18s; TRIP MACHINE 'BULGG2' AT 5.18s; TRIP MACHINE 'BULGBESS' AT 5.18s; TRIP BRANCH 'MURRA_HOTS' AT 5.2s; TRIP MACHINE 'WBTSG1' AT 5.2s; TRIP MACHINE 'WBTSG2' AT 5.2s; TRIP MACHINE 'WBTSG3' AT 5.2s; TRIP MACHINE 'WBTSG4' AT 5.2s; TRIP MACHINE 'WBTSG5' AT 5.2s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | TRIP MACHINE 'CROW' AT 5.18s removed since machine already out of service | TRIP BRANCH 'MURRA_HOTS¦NEAR' AT 5.2s; TRIP BRANCH 'MURRA_HOTS¦FAR' AT 5.2s; TRIP BRANCH 'MURRA_MRTS¦NEAR' AT 5.18s; TRIP BRANCH 'MURRA_MRTS¦FAR' AT 5.18s; TRIP BRANCH 'MURRA_KIAM¦NEAR' AT 5.18s; TRIP BRANCH 'MURRA_KIAM¦FAR' AT 5.18s | TRIP MACHINE 'WBTSG1' AT 5.2s; TRIP MACHINE 'WBTSG2' AT 5.2s; TRIP MACHINE 'WBTSG3' AT 5.2s; TRIP MACHINE 'WBTSG4' AT 5.2s; TRIP MACHINE 'WBTSG5' AT 5.2s | TRIP MACHINE 'CROW' AT 5.18s; TRIP MACHINE 'BULGG1' AT 5.18s; TRIP MACHINE 'BULGG2' AT 5.18s; TRIP MACHINE 'BULGBESS' AT 5.18s
CSR | Balanced Faults | SummerHigh | 21 |  | SummerHigh | SummerHigh_021 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'ELD220_THO220¦NEAR' AT 5.12s; TRIP BRANCH 'ELD220_THO220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'ELD220_THO220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 22 |  | SummerHigh | SummerHigh_022 | 100 | TRUE | TRUE | 0.077 | 1.087 | 1.087 | TRUE | 3 | 7 | 5 | 1.087 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 6.087s ↓ 0 | TRIP BRANCH 'GLEN66_WAR66¦NEAR' AT 5.077s; TRIP BRANCH 'GLEN66_WAR66¦FAR' AT 6.087s; APPLY FAULT TO BRANCH 'GLEN66_WAR66' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=1.087s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.077s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 6.087s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=1.087s, DISTANCE=0.01
CSR | Balanced Faults | SummerHigh | 23 |  | SummerHigh | SummerHigh_023 | 100 | TRUE | TRUE | 0.14 | 0.54 |  | FALSE | 3 | 7 | 5 | 0.54 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.54s ↓ 0 | TRIP BRANCH 'NUR66_SHEP66¦NEAR' AT 5.14s; TRIP BRANCH 'NUR66_SHEP66¦FAR' AT 5.54s; APPLY FAULT TO BRANCH 'NUR66_SHEP66' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.54s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.14s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.54s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.54s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerHigh | 24 |  | SummerHigh | SummerHigh_024 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerHigh | 25 |  | SummerHigh | SummerHigh_025 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'SHTS220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'SHTS220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerHigh | 26 |  | SummerHigh | SummerHigh_026 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerHigh | 27 |  | SummerHigh | SummerHigh_027 | 100 | TRUE | TRUE | 0.8 | 0.1 |  | FALSE | 3 | 4 | 5 | 0.8 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.8s ↓ 0 | TRIP BRANCH 'KE500_SM500¦NEAR' AT 5.8s; TRIP BRANCH 'KE500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'KE500_SM500¦NEAR' AT 8.8s; RESTORE BRANCH 'KE500_SM500¦FAR' AT 8.8s; APPLY FAULT TO BRANCH 'KE500_SM500' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.8s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerHigh | 28 |  | SummerHigh | SummerHigh_028 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerHigh | 29 |  | SummerHigh | SummerHigh_029 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'DE330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'DE330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=4, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerHigh | 30 |  | SummerHigh | SummerHigh_030 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'JIN330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'JIN330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'JIN330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'JIN330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'JIN330_WO330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerHigh | 31 |  | SummerHigh | SummerHigh_031 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_MUR330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_MUR330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_MUR330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerHigh | 32 |  | SummerHigh | SummerHigh_032 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_SM330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_SM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_SM330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerHigh | 33 |  | SummerHigh | SummerHigh_033 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_MUR330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_MUR330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_MUR330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerHigh | 34 |  | SummerHigh | SummerHigh_034 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_UPTM330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_UPTM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_UPTM330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerHigh | 35 |  | SummerHigh | SummerHigh_035 | 100 | TRUE | TRUE | 0.25 | 0.25 |  | FALSE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 5.25s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 5.25s; RESTORE BRANCH 'DEDTXDUMMY¦NEAR' AT 8.25s; RESTORE BRANCH 'DEDTXDUMMY¦FAR' AT 8.25s; APPLY FAULT TO BRANCH 'DEDTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.5 | Not active for this case P<400 MW (pickup is 1260 MW) | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦FAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦NEAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦FAR' AT 15s; TRIP SWITCHED_SHUNT 'DED' AT 15s
CSR | Balanced Faults | SummerHigh | 36 |  | SummerHigh | SummerHigh_036 | 100 | TRUE | TRUE | 0.1 | 0.1 |  | FALSE | 3 | 7 | 5 | 0.1 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.1s ↓ 0 | TRIP BRANCH 'SMTXDUMMY¦NEAR' AT 5.1s; TRIP BRANCH 'SMTXDUMMY¦FAR' AT 5.1s; RESTORE BRANCH 'SMTXDUMMY¦NEAR' AT 8.1s; RESTORE BRANCH 'SMTXDUMMY¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'SMTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.5
CSR | Balanced Faults | SummerHigh | 37 |  | SummerHigh | SummerHigh_037 | 100 | TRUE | TRUE | 0.43 | 0.43 |  | FALSE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHPTXDUMMY¦NEAR' AT 5.43s; TRIP BRANCH 'SHPTXDUMMY¦FAR' AT 5.43s; RESTORE BRANCH 'SHPTXDUMMY¦NEAR' AT 8.43s; RESTORE BRANCH 'SHPTXDUMMY¦FAR' AT 8.43s; APPLY FAULT TO BRANCH 'SHPTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.5
CSR | Plant Trip | SummerHigh | 38 |  | SummerHigh | SummerHigh_038 | 100 | TRUE | TRUE | 0 | 0 |  | FALSE | 3 |  | 5 | 0 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5s ↓ 0 | TRIP SWITCHED_SHUNT 'DED' AT 5.0s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=, RF_OFFSET=0, XF_OFFSET=0, DURATION=0s, DISTANCE=0.5
CSR | Balanced Faults | SummerHigh | 39 |  | SummerHigh | SummerHigh_039 | 100 | TRUE | TRUE | 0.08 | 0.08 |  | FALSE | 3 | 7 | 5 | 0.08 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.08s ↓ 0 | TRIP BRANCH 'LYB4¦NEAR' AT 5.08s; TRIP BRANCH 'LYB4¦FAR' AT 5.08s; RESTORE BRANCH 'LYB4¦NEAR' AT 8.08s; RESTORE BRANCH 'LYB4¦FAR' AT 8.08s; APPLY FAULT TO BRANCH 'LYB4' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.08s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.08s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.08s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.08s, DISTANCE=0.5
CSR | Plant Trip | SummerHigh | 40 |  | SummerHigh | SummerHigh_040 | 100 | TRUE | TRUE | 0 | 0 |  | FALSE | 3 |  | 5 | 0 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5s ↓ 0 | TRIP LOAD 'APD' AT 5s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=, RF_OFFSET=0, XF_OFFSET=0, DURATION=0s, DISTANCE=0.5

## Branch_Trips_SL2
Deliverable | Category | Model Name | Test No | Subtest No | Case | File_Name | Steps_Per_Write | PSSE | PSCAD | NEAR | FAR | CB FAIL | CB FAIL SCENARIO | RECLOSE | Fault_Type_sig | Fault_Time_sig | Fault_Duration_sig | Ures_sig | Zf2Zs_sig | Rf_Offset_sig | Xf_Offset_sig | Fault_X2R_sig | Distance | Generator Connected | Generator Disconnected | Fault_Timing_Signal_sig | PSSE Commands | Post_Init_Duration_s | Vslack_pu_sig | Model_Relpath | Original | Comment | Schemes | Schemes2 | Schemes3
CSR | Balanced Faults | SummerLow_Case2 | 1 |  | SummerLow_Case2 | SummerLow_Case2_001 | 100 | TRUE | TRUE | 0.43 | 0.12 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.43s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 2 |  | SummerLow_Case2 | SummerLow_Case2_002 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'SHTS220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'SHTS220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 3 |  | SummerLow_Case2 | SummerLow_Case2_003 | 100 | TRUE | TRUE | 0.43 | 0.12 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.43s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 4 |  | SummerLow_Case2 | SummerLow_Case2_004 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'DED220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'DED220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 5 |  | SummerLow_Case2 | SummerLow_Case2_005 | 100 | TRUE | TRUE | 0.08 | 0.1 | 0.175 | FALSE | 3 | 7 | 5 | 0.1 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.1s ↓ 0 | TRIP BRANCH 'HZ500_SM500¦NEAR' AT 5.08s; TRIP BRANCH 'HZ500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'HZ500_SM500¦NEAR' AT 8.08s; RESTORE BRANCH 'HZ500_SM500¦FAR' AT 8.08s; APPLY FAULT TO BRANCH 'HZ500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.08s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 6 |  | SummerLow_Case2 | SummerLow_Case2_006 | 100 | TRUE | TRUE | 0.175 | 0.175 | 0.175 | TRUE | 3 | 7 | 5 | 0.175 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.175s ↓ 0 | TRIP BRANCH 'RO500_SM500¦NEAR' AT 5.175s; TRIP BRANCH 'RO500_SM500¦FAR' AT 5.175s; APPLY FAULT TO BRANCH 'RO500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.175s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.175s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.175s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.175s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 7 |  | SummerLow_Case2 | SummerLow_Case2_007 | 100 | TRUE | TRUE | 0.8 | 0.1 | 0.175 | FALSE | 3 | 7 | 5 | 0.8 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.8s ↓ 0 | TRIP BRANCH 'KE500_SM500¦NEAR' AT 5.8s; TRIP BRANCH 'KE500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'KE500_SM500¦NEAR' AT 8.8s; RESTORE BRANCH 'KE500_SM500¦FAR' AT 8.8s; APPLY FAULT TO BRANCH 'KE500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.8s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 8 |  | SummerLow_Case2 | SummerLow_Case2_008 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 9 |  | SummerLow_Case2 | SummerLow_Case2_009 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'DE330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'DE330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=7, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 10 |  | SummerLow_Case2 | SummerLow_Case2_010 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'JIN330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'JIN330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'JIN330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'JIN330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'JIN330_WO330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 11 |  | SummerLow_Case2 | SummerLow_Case2_011 | 100 | TRUE | TRUE | 0.25 | 0.25 | 0.25 | TRUE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'DED330_MUR330¦NEAR' AT 5.25s; TRIP BRANCH 'DED330_MUR330¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'DED330_MUR330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.01 | Not active for this case P<400 MW (pickup is 1260 MW) | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦FAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦NEAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦FAR' AT 15s
CSR | Balanced Faults | SummerLow_Case2 | 12 |  | SummerLow_Case2 | SummerLow_Case2_012 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_SM330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_SM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_SM330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 13 |  | SummerLow_Case2 | SummerLow_Case2_013 | 100 | TRUE | TRUE | 0.25 | 0.25 | 0.25 | TRUE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'LWTM330_MUR330¦NEAR' AT 5.25s; TRIP BRANCH 'LWTM330_MUR330¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'LWTM330_MUR330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 14 |  | SummerLow_Case2 | SummerLow_Case2_014 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_UPTM330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_UPTM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_UPTM330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 15 |  | SummerLow_Case2 | SummerLow_Case2_015 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GLEN220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GLEN220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 16 |  | SummerLow_Case2 | SummerLow_Case2_016 | 100 | TRUE | TRUE | 0.43 | 0.43 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHEP220_GLEN220¦NEAR' AT 5.43s; TRIP BRANCH 'SHEP220_GLEN220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'SHEP220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 17 |  | SummerLow_Case2 | SummerLow_Case2_017 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHEP220_GLEN220¦NEAR' AT 5.12s; TRIP BRANCH 'SHEP220_GLEN220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'SHEP220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 18 |  | SummerLow_Case2 | SummerLow_Case2_018 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_MTB220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_MTB220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_MTB220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 19 |  | SummerLow_Case2 | SummerLow_Case2_019 | 100 | TRUE | TRUE | 0.43 | 0.43 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'FO220_SHEP220¦NEAR' AT 5.43s; TRIP BRANCH 'FO220_SHEP220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'FO220_SHEP220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 20 |  | SummerLow_Case2 | SummerLow_Case2_020 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01; TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; TRIP BRANCH 'MURRA_MRTS' AT 5.18s; TRIP BRANCH 'MURRA_KIAM' AT 5.18s; TRIP MACHINE 'BULGG1' AT 5.18s; TRIP MACHINE 'BULGG2' AT 5.18s; TRIP MACHINE 'BULGBESS' AT 5.18s; TRIP BRANCH 'MURRA_HOTS' AT 5.2s; TRIP MACHINE 'WBTSG1' AT 5.2s; TRIP MACHINE 'WBTSG2' AT 5.2s; TRIP MACHINE 'WBTSG3' AT 5.2s; TRIP MACHINE 'WBTSG4' AT 5.2s; TRIP MACHINE 'WBTSG5' AT 5.2s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | TRIP MACHINE 'CROW' AT 5.18s removed since machine already out of service | TRIP BRANCH 'MURRA_HOTS¦NEAR' AT 5.2s; TRIP BRANCH 'MURRA_HOTS¦FAR' AT 5.2s; TRIP BRANCH 'MURRA_MRTS¦NEAR' AT 5.18s; TRIP BRANCH 'MURRA_MRTS¦FAR' AT 5.18s; TRIP BRANCH 'MURRA_KIAM¦NEAR' AT 5.18s; TRIP BRANCH 'MURRA_KIAM¦FAR' AT 5.18s | TRIP MACHINE 'WBTSG1' AT 5.2s; TRIP MACHINE 'WBTSG2' AT 5.2s; TRIP MACHINE 'WBTSG3' AT 5.2s; TRIP MACHINE 'WBTSG4' AT 5.2s; TRIP MACHINE 'WBTSG5' AT 5.2s | TRIP MACHINE 'CROW' AT 5.18s; TRIP MACHINE 'BULGG1' AT 5.18s; TRIP MACHINE 'BULGG2' AT 5.18s; TRIP MACHINE 'BULGBESS' AT 5.18s
CSR | Balanced Faults | SummerLow_Case2 | 21 |  | SummerLow_Case2 | SummerLow_Case2_021 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'ELD220_THO220¦NEAR' AT 5.12s; TRIP BRANCH 'ELD220_THO220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'ELD220_THO220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 22 |  | SummerLow_Case2 | SummerLow_Case2_022 | 100 | TRUE | TRUE | 0.077 | 1.087 | 1.087 | TRUE | 3 | 7 | 5 | 1.087 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 6.087s ↓ 0 | TRIP BRANCH 'GLEN66_WAR66¦NEAR' AT 5.077s; TRIP BRANCH 'GLEN66_WAR66¦FAR' AT 6.087s; APPLY FAULT TO BRANCH 'GLEN66_WAR66' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=1.087s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.077s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 6.087s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=1.087s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case2 | 23 |  | SummerLow_Case2 | SummerLow_Case2_023 | 100 | TRUE | TRUE | 0.14 | 0.54 |  | FALSE | 3 | 7 | 5 | 0.54 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.54s ↓ 0 | TRIP BRANCH 'NUR66_SHEP66¦NEAR' AT 5.14s; TRIP BRANCH 'NUR66_SHEP66¦FAR' AT 5.54s; APPLY FAULT TO BRANCH 'NUR66_SHEP66' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.54s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.14s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.54s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.54s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case2 | 24 |  | SummerLow_Case2 | SummerLow_Case2_024 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case2 | 25 |  | SummerLow_Case2 | SummerLow_Case2_025 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'SHTS220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'SHTS220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerLow_Case2 | 26 |  | SummerLow_Case2 | SummerLow_Case2_026 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case2 | 27 |  | SummerLow_Case2 | SummerLow_Case2_027 | 100 | TRUE | TRUE | 0.8 | 0.1 |  | FALSE | 3 | 4 | 5 | 0.8 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.8s ↓ 0 | TRIP BRANCH 'KE500_SM500¦NEAR' AT 5.8s; TRIP BRANCH 'KE500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'KE500_SM500¦NEAR' AT 8.8s; RESTORE BRANCH 'KE500_SM500¦FAR' AT 8.8s; APPLY FAULT TO BRANCH 'KE500_SM500' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.8s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case2 | 28 |  | SummerLow_Case2 | SummerLow_Case2_028 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerLow_Case2 | 29 |  | SummerLow_Case2 | SummerLow_Case2_029 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'DE330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'DE330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=4, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case2 | 30 |  | SummerLow_Case2 | SummerLow_Case2_030 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'JIN330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'JIN330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'JIN330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'JIN330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'JIN330_WO330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case2 | 31 |  | SummerLow_Case2 | SummerLow_Case2_031 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_MUR330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_MUR330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_MUR330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerLow_Case2 | 32 |  | SummerLow_Case2 | SummerLow_Case2_032 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_SM330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_SM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_SM330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerLow_Case2 | 33 |  | SummerLow_Case2 | SummerLow_Case2_033 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_MUR330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_MUR330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_MUR330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case2 | 34 |  | SummerLow_Case2 | SummerLow_Case2_034 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_UPTM330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_UPTM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_UPTM330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case2 | 35 |  | SummerLow_Case2 | SummerLow_Case2_035 | 100 | TRUE | TRUE | 0.25 | 0.25 |  | FALSE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 5.25s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 5.25s; RESTORE BRANCH 'DEDTXDUMMY¦NEAR' AT 8.25s; RESTORE BRANCH 'DEDTXDUMMY¦FAR' AT 8.25s; APPLY FAULT TO BRANCH 'DEDTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.5 | Not active for this case P<400 MW (pickup is 1260 MW) | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦FAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦NEAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦FAR' AT 15s; TRIP SWITCHED_SHUNT 'DED' AT 15s
CSR | Balanced Faults | SummerLow_Case2 | 36 |  | SummerLow_Case2 | SummerLow_Case2_036 | 100 | TRUE | TRUE | 0.1 | 0.1 |  | FALSE | 3 | 7 | 5 | 0.1 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.1s ↓ 0 | TRIP BRANCH 'SMTXDUMMY¦NEAR' AT 5.1s; TRIP BRANCH 'SMTXDUMMY¦FAR' AT 5.1s; RESTORE BRANCH 'SMTXDUMMY¦NEAR' AT 8.1s; RESTORE BRANCH 'SMTXDUMMY¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'SMTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.5
CSR | Balanced Faults | SummerLow_Case2 | 37 |  | SummerLow_Case2 | SummerLow_Case2_037 | 100 | TRUE | TRUE | 0.43 | 0.43 |  | FALSE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHPTXDUMMY¦NEAR' AT 5.43s; TRIP BRANCH 'SHPTXDUMMY¦FAR' AT 5.43s; RESTORE BRANCH 'SHPTXDUMMY¦NEAR' AT 8.43s; RESTORE BRANCH 'SHPTXDUMMY¦FAR' AT 8.43s; APPLY FAULT TO BRANCH 'SHPTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.5
CSR | Plant Trip | SummerLow_Case2 | 38 |  | SummerLow_Case2 | SummerLow_Case2_038 | 100 | TRUE | TRUE | 0 | 0 |  | FALSE | 3 |  | 5 | 0 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5s ↓ 0 | TRIP SWITCHED_SHUNT 'DED' AT 5.0s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=, RF_OFFSET=0, XF_OFFSET=0, DURATION=0s, DISTANCE=0.5
CSR | Balanced Faults | SummerLow_Case2 | 39 |  | SummerLow_Case2 | SummerLow_Case2_039 | 100 | TRUE | TRUE | 0.08 | 0.08 |  | FALSE | 3 | 7 | 5 | 0.08 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.08s ↓ 0 | TRIP BRANCH 'LYB4¦NEAR' AT 5.08s; TRIP BRANCH 'LYB4¦FAR' AT 5.08s; RESTORE BRANCH 'LYB4¦NEAR' AT 8.08s; RESTORE BRANCH 'LYB4¦FAR' AT 8.08s; APPLY FAULT TO BRANCH 'LYB4' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.08s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.08s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.08s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.08s, DISTANCE=0.5
CSR | Plant Trip | SummerLow_Case2 | 40 |  | SummerLow_Case2 | SummerLow_Case2_040 | 100 | TRUE | TRUE | 0 | 0 |  | FALSE | 3 |  | 5 | 0 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5s ↓ 0 | TRIP LOAD 'APD' AT 5s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=, RF_OFFSET=0, XF_OFFSET=0, DURATION=0s, DISTANCE=0.5

## Branch_Trips_SL1
Deliverable | Category | Model Name | Test No | Subtest No | Case | File_Name | Steps_Per_Write | PSSE | PSCAD | NEAR | FAR | CB FAIL | CB FAIL SCENARIO | RECLOSE | Fault_Type_sig | Fault_Time_sig | Fault_Duration_sig | Ures_sig | Zf2Zs_sig | Rf_Offset_sig | Xf_Offset_sig | Fault_X2R_sig | Distance | Generator Connected | Generator Disconnected | Fault_Timing_Signal_sig | PSSE Commands | Post_Init_Duration_s | Vslack_pu_sig | Model_Relpath | Original | Comment | Schemes | Schemes2 | Schemes3
CSR | Balanced Faults | SummerLow_Case1 | 1 |  | SummerLow_Case1 | SummerLow_Case1_001 | 100 | TRUE | TRUE | 0.43 | 0.12 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.43s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 2 |  | SummerLow_Case1 | SummerLow_Case1_002 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'SHTS220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'SHTS220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 3 |  | SummerLow_Case1 | SummerLow_Case1_003 | 100 | TRUE | TRUE | 0.43 | 0.12 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.43s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 4 |  | SummerLow_Case1 | SummerLow_Case1_004 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'DED220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'DED220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 5 |  | SummerLow_Case1 | SummerLow_Case1_005 | 100 | TRUE | TRUE | 0.08 | 0.1 | 0.175 | FALSE | 3 | 7 | 5 | 0.1 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.1s ↓ 0 | TRIP BRANCH 'HZ500_SM500¦NEAR' AT 5.08s; TRIP BRANCH 'HZ500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'HZ500_SM500¦NEAR' AT 8.08s; RESTORE BRANCH 'HZ500_SM500¦FAR' AT 8.08s; APPLY FAULT TO BRANCH 'HZ500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.08s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 6 |  | SummerLow_Case1 | SummerLow_Case1_006 | 100 | TRUE | TRUE | 0.175 | 0.175 | 0.175 | TRUE | 3 | 7 | 5 | 0.175 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.175s ↓ 0 | TRIP BRANCH 'RO500_SM500¦NEAR' AT 5.175s; TRIP BRANCH 'RO500_SM500¦FAR' AT 5.175s; APPLY FAULT TO BRANCH 'RO500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.175s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.175s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.175s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.175s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 7 |  | SummerLow_Case1 | SummerLow_Case1_007 | 100 | TRUE | TRUE | 0.8 | 0.1 | 0.175 | FALSE | 3 | 7 | 5 | 0.8 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.8s ↓ 0 | TRIP BRANCH 'KE500_SM500¦NEAR' AT 5.8s; TRIP BRANCH 'KE500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'KE500_SM500¦NEAR' AT 8.8s; RESTORE BRANCH 'KE500_SM500¦FAR' AT 8.8s; APPLY FAULT TO BRANCH 'KE500_SM500' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.8s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 8 |  | SummerLow_Case1 | SummerLow_Case1_008 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 9 |  | SummerLow_Case1 | SummerLow_Case1_009 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'DE330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'DE330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=7, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 10 |  | SummerLow_Case1 | SummerLow_Case1_010 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'JIN330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'JIN330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'JIN330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'JIN330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'JIN330_WO330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 11 |  | SummerLow_Case1 | SummerLow_Case1_011 | 100 | TRUE | TRUE | 0.25 | 0.25 | 0.25 | TRUE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'DED330_MUR330¦NEAR' AT 5.25s; TRIP BRANCH 'DED330_MUR330¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'DED330_MUR330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.01 | Not active for this case P<400 MW (pickup is 1260 MW) | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦FAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦NEAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦FAR' AT 15s
CSR | Balanced Faults | SummerLow_Case1 | 12 |  | SummerLow_Case1 | SummerLow_Case1_012 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_SM330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_SM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_SM330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 13 |  | SummerLow_Case1 | SummerLow_Case1_013 | 100 | TRUE | TRUE | 0.25 | 0.25 | 0.25 | TRUE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'LWTM330_MUR330¦NEAR' AT 5.25s; TRIP BRANCH 'LWTM330_MUR330¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'LWTM330_MUR330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 14 |  | SummerLow_Case1 | SummerLow_Case1_014 | 100 | TRUE | TRUE | 0.1 | 0.12 | 0.25 | FALSE | 3 | 7 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_UPTM330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_UPTM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_UPTM330' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 15 |  | SummerLow_Case1 | SummerLow_Case1_015 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GLEN220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GLEN220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 16 |  | SummerLow_Case1 | SummerLow_Case1_016 | 100 | TRUE | TRUE | 0.43 | 0.43 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHEP220_GLEN220¦NEAR' AT 5.43s; TRIP BRANCH 'SHEP220_GLEN220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'SHEP220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 17 |  | SummerLow_Case1 | SummerLow_Case1_017 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHEP220_GLEN220¦NEAR' AT 5.12s; TRIP BRANCH 'SHEP220_GLEN220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'SHEP220_GLEN220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 18 |  | SummerLow_Case1 | SummerLow_Case1_018 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_MTB220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_MTB220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_MTB220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 19 |  | SummerLow_Case1 | SummerLow_Case1_019 | 100 | TRUE | TRUE | 0.43 | 0.43 | 0.43 | TRUE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'FO220_SHEP220¦NEAR' AT 5.43s; TRIP BRANCH 'FO220_SHEP220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'FO220_SHEP220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 20 |  | SummerLow_Case1 | SummerLow_Case1_020 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01; TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; TRIP BRANCH 'MURRA_MRTS' AT 5.18s; TRIP BRANCH 'MURRA_KIAM' AT 5.18s; TRIP MACHINE 'BULGG1' AT 5.18s; TRIP MACHINE 'BULGG2' AT 5.18s; TRIP MACHINE 'BULGBESS' AT 5.18s; TRIP BRANCH 'MURRA_HOTS' AT 5.2s; TRIP MACHINE 'WBTSG1' AT 5.2s; TRIP MACHINE 'WBTSG2' AT 5.2s; TRIP MACHINE 'WBTSG3' AT 5.2s; TRIP MACHINE 'WBTSG4' AT 5.2s; TRIP MACHINE 'WBTSG5' AT 5.2s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | TRIP MACHINE 'CROW' AT 5.18s removed since machine already out of service | TRIP BRANCH 'MURRA_HOTS¦NEAR' AT 5.2s; TRIP BRANCH 'MURRA_HOTS¦FAR' AT 5.2s; TRIP BRANCH 'MURRA_MRTS¦NEAR' AT 5.18s; TRIP BRANCH 'MURRA_MRTS¦FAR' AT 5.18s; TRIP BRANCH 'MURRA_KIAM¦NEAR' AT 5.18s; TRIP BRANCH 'MURRA_KIAM¦FAR' AT 5.18s | TRIP MACHINE 'WBTSG1' AT 5.2s; TRIP MACHINE 'WBTSG2' AT 5.2s; TRIP MACHINE 'WBTSG3' AT 5.2s; TRIP MACHINE 'WBTSG4' AT 5.2s; TRIP MACHINE 'WBTSG5' AT 5.2s | TRIP MACHINE 'CROW' AT 5.18s; TRIP MACHINE 'BULGG1' AT 5.18s; TRIP MACHINE 'BULGG2' AT 5.18s; TRIP MACHINE 'BULGBESS' AT 5.18s
CSR | Balanced Faults | SummerLow_Case1 | 21 |  | SummerLow_Case1 | SummerLow_Case1_021 | 100 | TRUE | TRUE | 0.12 | 0.22 | 0.43 | FALSE | 3 | 7 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'ELD220_THO220¦NEAR' AT 5.12s; TRIP BRANCH 'ELD220_THO220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'ELD220_THO220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 22 |  | SummerLow_Case1 | SummerLow_Case1_022 | 100 | TRUE | TRUE | 0.077 | 1.087 | 1.087 | TRUE | 3 | 7 | 5 | 1.087 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 6.087s ↓ 0 | TRIP BRANCH 'GLEN66_WAR66¦NEAR' AT 5.077s; TRIP BRANCH 'GLEN66_WAR66¦FAR' AT 6.087s; APPLY FAULT TO BRANCH 'GLEN66_WAR66' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=1.087s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.077s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 6.087s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=1.087s, DISTANCE=0.01
CSR | Balanced Faults | SummerLow_Case1 | 23 |  | SummerLow_Case1 | SummerLow_Case1_023 | 100 | TRUE | TRUE | 0.14 | 0.54 |  | FALSE | 3 | 7 | 5 | 0.54 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.54s ↓ 0 | TRIP BRANCH 'NUR66_SHEP66¦NEAR' AT 5.14s; TRIP BRANCH 'NUR66_SHEP66¦FAR' AT 5.54s; APPLY FAULT TO BRANCH 'NUR66_SHEP66' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.54s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.14s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.54s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.54s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case1 | 24 |  | SummerLow_Case1 | SummerLow_Case1_024 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case1 | 25 |  | SummerLow_Case1 | SummerLow_Case1_025 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'SHTS220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'SHTS220_GESF220¦FAR' AT 5.22s; RESTORE BRANCH 'SHTS220_GESF220¦NEAR' AT 8.12s; RESTORE BRANCH 'SHTS220_GESF220¦FAR' AT 8.12s; APPLY FAULT TO BRANCH 'SHTS220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerLow_Case1 | 26 |  | SummerLow_Case1 | SummerLow_Case1_026 | 100 | TRUE | TRUE | 0.12 | 0.22 |  | FALSE | 3 | 4 | 5 | 0.22 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.22s ↓ 0 | TRIP BRANCH 'DED220_GESF220¦NEAR' AT 5.12s; TRIP BRANCH 'DED220_GESF220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'DED220_GESF220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.12s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.22s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.22s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case1 | 27 |  | SummerLow_Case1 | SummerLow_Case1_027 | 100 | TRUE | TRUE | 0.8 | 0.1 |  | FALSE | 3 | 4 | 5 | 0.8 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.8s ↓ 0 | TRIP BRANCH 'KE500_SM500¦NEAR' AT 5.8s; TRIP BRANCH 'KE500_SM500¦FAR' AT 5.1s; RESTORE BRANCH 'KE500_SM500¦NEAR' AT 8.8s; RESTORE BRANCH 'KE500_SM500¦FAR' AT 8.8s; APPLY FAULT TO BRANCH 'KE500_SM500' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.8s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.8s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case1 | 28 |  | SummerLow_Case1 | SummerLow_Case1_028 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerLow_Case1 | 29 |  | SummerLow_Case1 | SummerLow_Case1_029 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DE330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'DE330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'DE330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'DE330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'DE330_WO330' AT 5s WITH TYPE=4, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case1 | 30 |  | SummerLow_Case1 | SummerLow_Case1_030 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'JIN330_WO330¦NEAR' AT 5.1s; TRIP BRANCH 'JIN330_WO330¦FAR' AT 5.12s; RESTORE BRANCH 'JIN330_WO330¦NEAR' AT 8.1s; RESTORE BRANCH 'JIN330_WO330¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'JIN330_WO330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case1 | 31 |  | SummerLow_Case1 | SummerLow_Case1_031 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_MUR330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_MUR330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_MUR330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerLow_Case1 | 32 |  | SummerLow_Case1 | SummerLow_Case1_032 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.01 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'DED330_SM330¦NEAR' AT 5.1s; TRIP BRANCH 'DED330_SM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'DED330_SM330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.01
CSR | Unbalanced Faults | SummerLow_Case1 | 33 |  | SummerLow_Case1 | SummerLow_Case1_033 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_MUR330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_MUR330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_MUR330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Unbalanced Faults | SummerLow_Case1 | 34 |  | SummerLow_Case1 | SummerLow_Case1_034 | 100 | TRUE | TRUE | 0.1 | 0.12 |  | FALSE | 3 | 4 | 5 | 0.12 |  | 0 | 0 | 0 | 10 | 0.99 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.12s ↓ 0 | TRIP BRANCH 'LWTM330_UPTM330¦NEAR' AT 5.1s; TRIP BRANCH 'LWTM330_UPTM330¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'LWTM330_UPTM330' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.12s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=4, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.12s, DISTANCE=0.99
CSR | Balanced Faults | SummerLow_Case1 | 35 |  | SummerLow_Case1 | SummerLow_Case1_035 | 100 | TRUE | TRUE | 0.25 | 0.25 |  | FALSE | 3 | 7 | 5 | 0.25 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.25s ↓ 0 | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 5.25s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 5.25s; RESTORE BRANCH 'DEDTXDUMMY¦NEAR' AT 8.25s; RESTORE BRANCH 'DEDTXDUMMY¦FAR' AT 8.25s; APPLY FAULT TO BRANCH 'DEDTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.25s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.25s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.25s, DISTANCE=0.5 | Not active for this case P<400 MW (pickup is 1260 MW) | TRIP BRANCH 'DEDTXDUMMY¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY¦FAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦NEAR' AT 15s; TRIP BRANCH 'DEDTXDUMMY2¦FAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦NEAR' AT 15s; TRIP BRANCH 'DED330_MUR330No2¦FAR' AT 15s; TRIP SWITCHED_SHUNT 'DED' AT 15s
CSR | Balanced Faults | SummerLow_Case1 | 36 |  | SummerLow_Case1 | SummerLow_Case1_036 | 100 | TRUE | TRUE | 0.1 | 0.1 |  | FALSE | 3 | 7 | 5 | 0.1 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.1s ↓ 0 | TRIP BRANCH 'SMTXDUMMY¦NEAR' AT 5.1s; TRIP BRANCH 'SMTXDUMMY¦FAR' AT 5.1s; RESTORE BRANCH 'SMTXDUMMY¦NEAR' AT 8.1s; RESTORE BRANCH 'SMTXDUMMY¦FAR' AT 8.1s; APPLY FAULT TO BRANCH 'SMTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.1s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.1s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.1s, DISTANCE=0.5
CSR | Balanced Faults | SummerLow_Case1 | 37 |  | SummerLow_Case1 | SummerLow_Case1_037 | 100 | TRUE | TRUE | 0.43 | 0.43 |  | FALSE | 3 | 7 | 5 | 0.43 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.43s ↓ 0 | TRIP BRANCH 'SHPTXDUMMY¦NEAR' AT 5.43s; TRIP BRANCH 'SHPTXDUMMY¦FAR' AT 5.43s; RESTORE BRANCH 'SHPTXDUMMY¦NEAR' AT 8.43s; RESTORE BRANCH 'SHPTXDUMMY¦FAR' AT 8.43s; APPLY FAULT TO BRANCH 'SHPTXDUMMY' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.43s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.43s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.43s, DISTANCE=0.5
CSR | Plant Trip | SummerLow_Case1 | 38 |  | SummerLow_Case1 | SummerLow_Case1_038 | 100 | TRUE | TRUE | 0 | 0 |  | FALSE | 3 |  | 5 | 0 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5s ↓ 0 | TRIP SWITCHED_SHUNT 'DED' AT 5.0s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=, RF_OFFSET=0, XF_OFFSET=0, DURATION=0s, DISTANCE=0.5
CSR | Balanced Faults | SummerLow_Case1 | 39 |  | SummerLow_Case1 | SummerLow_Case1_039 | 100 | TRUE | TRUE | 0.08 | 0.08 |  | FALSE | 3 | 7 | 5 | 0.08 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5.08s ↓ 0 | TRIP BRANCH 'LYB4¦NEAR' AT 5.08s; TRIP BRANCH 'LYB4¦FAR' AT 5.08s; RESTORE BRANCH 'LYB4¦NEAR' AT 8.08s; RESTORE BRANCH 'LYB4¦FAR' AT 8.08s; APPLY FAULT TO BRANCH 'LYB4' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.08s, DISTANCE=0.5 | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5.08s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5.08s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=7, RF_OFFSET=0, XF_OFFSET=0, DURATION=0.08s, DISTANCE=0.5
CSR | Plant Trip | SummerLow_Case1 | 40 |  | SummerLow_Case1 | SummerLow_Case1_040 | 100 | TRUE | TRUE | 0 | 0 |  | FALSE | 3 |  | 5 | 0 |  | 0 | 0 | 0 | 10 | 0.5 | TRUE | TRUE | 0, AT 5s ↑ 1, at 5s ↓ 0 | TRIP LOAD 'APD' AT 5s | 20 |  |  | TRIP BRANCH 'BAL220_WAR220¦NEAR' AT 5s; TRIP BRANCH 'BAL220_WAR220¦FAR' AT 5s; APPLY FAULT TO BRANCH 'BAL220_WAR220' AT 5s WITH TYPE=, RF_OFFSET=0, XF_OFFSET=0, DURATION=0s, DISTANCE=0.5

## 52513_Vref
Deliverable | Category | Figure Number | Clause | Test No | Subtest No | Case | File_Name | Steps_Per_Write | PSSE | PSCAD | Grid_SCR | Grid_FL_MVA_sig | Grid_X2R_sig | Vpoc_pu_sig | Qpoc_pu | Qpoc_MVAr_sig | Vref_init | Ppoc_pu | Ppoc_MW_sig | PSSE Commands | Post_Init_Duration_s | Vslack_pu_sig | Model_Relpath | Test Details | Vpoc_disturbance_pu_sig | U_Ov
CSR | Vref Steps | 1 |  | 1 |  | SummerLow_Case1 | SummerLow_Case1_CSR_VrefSteps_001_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.0101668 AT 5s | 30 |  |  | Vref change -5% (sat)
CSR | Vref Steps | 2 |  | 2 |  | SummerLow_Case1 | SummerLow_Case1_CSR_VrefSteps_002_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.1101668 AT 5s | 30 |  |  | Vref change +5%
CSR | Vref Steps | 3 |  | 3 |  | SummerLow_Case1 | SummerLow_Case1_CSR_VrefSteps_003_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.0351668 AT 5s;SET MODEL 'ppc' VAR 16 TO 1.1101668 AT 10s | 30 |  |  | Vref change -2.5%, +5%
CSR | Vref Steps | 4 |  | 4 |  | SummerLow_Case1 | SummerLow_Case1_CSR_VrefSteps_004_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.0851668 AT 5s;SET MODEL 'ppc' VAR 16 TO 1.0101668 AT 10s | 30 |  |  | Vref change +2.5%, -5%
CSR | Vref Steps | 1 |  | 1 |  | SummerLow_Case2 | SummerLow_Case2_CSR_VrefSteps_001_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.010488 AT 5s | 30 |  |  | Vref change -5% (sat)
CSR | Vref Steps | 2 |  | 2 |  | SummerLow_Case2 | SummerLow_Case2_CSR_VrefSteps_002_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.110488 AT 5s | 30 |  |  | Vref change +5%
CSR | Vref Steps | 3 |  | 3 |  | SummerLow_Case2 | SummerLow_Case2_CSR_VrefSteps_003_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.035488 AT 5s;SET MODEL 'ppc' VAR 16 TO 1.110488 AT 10s | 30 |  |  | Vref change -2.5%, +5%
CSR | Vref Steps | 4 |  | 4 |  | SummerLow_Case2 | SummerLow_Case2_CSR_VrefSteps_004_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.085488 AT 5s;SET MODEL 'ppc' VAR 16 TO 1.010488 AT 10s | 30 |  |  | Vref change +2.5%, -5%
CSR | Vref Steps | 1 |  | 1 |  | SummerHigh | SummerHigh_CSR_VrefSteps_001_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.01028 AT 5s | 30 |  |  | Vref change -5% (sat)
CSR | Vref Steps | 2 |  | 2 |  | SummerHigh | SummerHigh_CSR_VrefSteps_002_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.11028 AT 5s | 30 |  |  | Vref change +5%
CSR | Vref Steps | 3 |  | 3 |  | SummerHigh | SummerHigh_CSR_VrefSteps_003_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.03528 AT 5s;SET MODEL 'ppc' VAR 16 TO 1.11028 AT 10s | 30 |  |  | Vref change -2.5%, +5%
CSR | Vref Steps | 4 |  | 4 |  | SummerHigh | SummerHigh_CSR_VrefSteps_004_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | SET MODEL 'ppc' VAR 16 TO 1.08528 AT 5s;SET MODEL 'ppc' VAR 16 TO 1.01028 AT 10s | 30 |  |  | Vref change +2.5%, -5%

## 52513_Qref
Deliverable | Category | Figure Number | Clause | Test No | Subtest No | Case | File_Name | Steps_Per_Write | PSSE | PSCAD | Grid_SCR | Grid_FL_MVA_sig | Grid_X2R_sig | Vpoc_pu_sig | Qpoc_pu | Qpoc_MVAr_sig | Vref_init | Ppoc_pu | Ppoc_MW_sig | PSSE Commands | Post_Init_Duration_s | Vslack_pu_sig | Test Details | Model_Relpath | Vpoc_disturbance_pu_sig | U_Ov | Signal1 | Signal2 | T1 | T2
CSR | Qref Steps | 1 |  | 1 |  | SummerLow_Case1 | SummerLow_Case1_CSR_QrefSteps_001_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↓ -0.926156962025316,WITH SCALING=98750 | 30 |  | Qref -0.926156962025316p.u at 5s |  |  |  | -0.92616 | 0 | 5 | 0
CSR | Qref Steps | 2 |  | 2 |  | SummerLow_Case1 | SummerLow_Case1_CSR_QrefSteps_002_P1_Q-0.43_V2.077 | 100 | TRUE | TRUE | NA | NA | NA | 2.077 | -0.42616 | -42.083 | 2.0602 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↑ 0.0738430379746836,WITH SCALING=98750 | 30 |  | Qref 0.0738430379746836p.u at 5s |  |  |  | 0.073843 | 0 | 5 | 0
CSR | Qref Steps | 3 |  | 3 |  | SummerLow_Case1 | SummerLow_Case1_CSR_QrefSteps_003_P1_Q-0.43_V3.077 | 100 | TRUE | TRUE | NA | NA | NA | 3.077 | -0.42616 | -42.083 | 3.0602 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↓ -0.676156962025316, AT 15s ↑ 0.0738430379746836, WITH SCALING=98750 | 30 |  | Qref -0.676156962025316pu at 5s, 0.0738430379746836pu at 15s |  |  |  | -0.67616 | 0.073843 | 5 | 15
CSR | Qref Steps | 4 |  | 4 |  | SummerLow_Case1 | SummerLow_Case1_CSR_QrefSteps_004_P1_Q-0.43_V4.077 | 100 | TRUE | TRUE | NA | NA | NA | 4.077 | -0.42616 | -42.083 | 4.0602 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↑ -0.176156962025316, AT 15s ↓ -0.926156962025316, WITH SCALING=98750 | 30 |  | Qref -0.176156962025316pu at 5s, -0.926156962025316pu at 15s |  |  |  | -0.17616 | -0.92616 | 5 | 15
CSR | Qref Steps | 1 |  | 1 |  | SummerLow_Case2 | SummerLow_Case2_CSR_QrefSteps_001_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↓ -0.662329113924051,WITH SCALING=98750 | 30 |  | Qref -0.662329113924051p.u at 5s |  |  |  | -0.66233 | 0 | 5 | 0
CSR | Qref Steps | 2 |  | 2 |  | SummerLow_Case2 | SummerLow_Case2_CSR_QrefSteps_002_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↑ 0.337670886075949,WITH SCALING=98750 | 30 |  | Qref 0.337670886075949p.u at 5s |  |  |  | 0.33767 | 0 | 5 | 0
CSR | Qref Steps | 3 |  | 3 |  | SummerLow_Case2 | SummerLow_Case2_CSR_QrefSteps_003_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↓ -0.412329113924051, AT 15s ↑ 0.337670886075949, WITH SCALING=98750 | 30 |  | Qref -0.412329113924051pu at 5s, 0.337670886075949pu at 15s |  |  |  | -0.41233 | 0.33767 | 5 | 15
CSR | Qref Steps | 4 |  | 4 |  | SummerLow_Case2 | SummerLow_Case2_CSR_QrefSteps_004_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↑ 0.0876708860759494, AT 15s ↓ -0.662329113924051, WITH SCALING=98750 | 30 |  | Qref 0.0876708860759494pu at 5s, -0.662329113924051pu at 15s |  |  |  | 0.087671 | -0.66233 | 5 | 15
CSR | Qref Steps | 1 |  | 1 |  | SummerHigh | SummerHigh_CSR_QrefSteps_001_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↓ -0.771392405063291,WITH SCALING=98750 | 30 |  | Qref -0.771392405063291p.u at 5s |  |  |  | -0.77139 | 0 | 5 | 0
CSR | Qref Steps | 2 |  | 2 |  | SummerHigh | SummerHigh_CSR_QrefSteps_002_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↑ 0.228607594936709,WITH SCALING=98750 | 30 |  | Qref 0.228607594936709p.u at 5s |  |  |  | 0.22861 | 0 | 5 | 0
CSR | Qref Steps | 3 |  | 3 |  | SummerHigh | SummerHigh_CSR_QrefSteps_003_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↓ -0.521392405063291, AT 15s ↑ 0.228607594936709, WITH SCALING=98750 | 30 |  | Qref -0.521392405063291pu at 5s, 0.228607594936709pu at 15s |  |  |  | -0.52139 | 0.22861 | 5 | 15
CSR | Qref Steps | 4 |  | 4 |  | SummerHigh | SummerHigh_CSR_QrefSteps_004_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | SET MODEL 'ppc' CON 161 TO 303 AT 0s; DRIVE MODEL 'ppc' VAR 14 = AT 5s ↑ -0.0213924050632912, AT 15s ↓ -0.771392405063291, WITH SCALING=98750 | 30 |  | Qref -0.0213924050632912pu at 5s, -0.771392405063291pu at 15s |  |  |  | -0.021392 | -0.77139 | 5 | 15

## 52513_PFref
Deliverable | Category | Figure Number | Clause | Test No | Subtest No | Case | File_Name | Steps_Per_Write | PSSE | PSCAD | Grid_SCR | Grid_FL_MVA_sig | Grid_X2R_sig | Vpoc_pu_sig | Qpoc_pu | Qpoc_MVAr_sig | Vref_init | Ppoc_pu | Ppoc_MW_sig | 0.5Q_PF_target | 0.25Q_PF_target | 1.25Q_PF_target | PSSE Commands | Post_Init_Duration_s | Vslack_pu_sig | Test Details | Model_Relpath | Vpoc_disturbance_pu_sig | U_Ov
CSR | PFref Steps | 1 |  | 1 |  | SummerLow_Case1 | SummerLow_Case1_CSR_PFrefSteps_001_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ 1.0, WITH SCALING=0.981049498258603 | 30 | 1.0056 | PFref 0.5pu at 5s
CSR | PFref Steps | 2 |  | 2 |  | SummerLow_Case1 | SummerLow_Case1_CSR_PFrefSteps_002_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ -1.0, WITH SCALING=0.981049498258603 | 30 | 1.0489 | PFref -0.5pu at 5s
CSR | PFref Steps | 3 |  | 3 |  | SummerLow_Case1 | SummerLow_Case1_CSR_PFrefSteps_003_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ 1.0, AT 15s ↑ 0.935177364792967, WITH SCALING=0.95881020276312 | 30 | 1.0056 | PFref 0.5pu at 5s, 1.5pu at 15s
CSR | PFref Steps | 4 |  | 4 |  | SummerLow_Case1 | SummerLow_Case1_CSR_PFrefSteps_004_P1_Q-0.43_V1.077 | 100 | TRUE | TRUE | NA | NA | NA | 1.077 | -0.42616 | -42.083 | 1.0602 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ -1.0, AT 15s ↑ -0.935177364792967, WITH SCALING=0.95881020276312 | 30 | 1.0923 | PFref -0.5pu at 5s, -1.5pu at 15s
CSR | PFref Steps | 1 |  | 1 |  | SummerLow_Case2 | SummerLow_Case2_CSR_PFrefSteps_001_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ 1.0, WITH SCALING=0.981049498258603 | 30 |  | PFref 0.5pu at 5s
CSR | PFref Steps | 2 |  | 2 |  | SummerLow_Case2 | SummerLow_Case2_CSR_PFrefSteps_002_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ -1.0, WITH SCALING=0.981049498258603 | 30 |  | PFref -0.5pu at 5s
CSR | PFref Steps | 3 |  | 3 |  | SummerLow_Case2 | SummerLow_Case2_CSR_PFrefSteps_003_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ 1.0, AT 15s ↑ 0.935177364792967, WITH SCALING=0.95881020276312 | 30 |  | PFref 0.5pu at 5s, 1.5pu at 15s
CSR | PFref Steps | 4 |  | 4 |  | SummerLow_Case2 | SummerLow_Case2_CSR_PFrefSteps_004_P1_Q-0.16_V1.0669 | 100 | TRUE | TRUE | NA | NA | NA | 1.0669 | -0.16233 | -16.03 | 1.0605 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ -1.0, AT 15s ↑ -0.935177364792967, WITH SCALING=0.95881020276312 | 30 |  | PFref -0.5pu at 5s, -1.5pu at 15s
CSR | PFref Steps | 1 |  | 1 |  | SummerHigh | SummerHigh_CSR_PFrefSteps_001_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ 1.0, WITH SCALING=0.981049498258603 | 30 |  | PFref 0.5pu at 5s
CSR | PFref Steps | 2 |  | 2 |  | SummerHigh | SummerHigh_CSR_PFrefSteps_002_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ -1.0, WITH SCALING=0.981049498258603 | 30 |  | PFref -0.5pu at 5s
CSR | PFref Steps | 3 |  | 3 |  | SummerHigh | SummerHigh_CSR_PFrefSteps_003_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ 1.0, AT 15s ↑ 0.935177364792967, WITH SCALING=0.95881020276312 | 30 |  | PFref 0.5pu at 5s, 1.5pu at 15s
CSR | PFref Steps | 4 |  | 4 |  | SummerHigh | SummerHigh_CSR_PFrefSteps_004_P1_Q-0.27_V1.071 | 100 | TRUE | TRUE | NA | NA | NA | 1.071 | -0.27139 | -26.8 | 1.0603 | 1 | 250 | 0.98105 | 0.95881 | 0.89666 | SET MODEL 'ppc' CON 161 TO 1074 AT 0s; DRIVE MODEL 'ppc' VAR 15 = AT 5s ↑ -1.0, AT 15s ↑ -0.935177364792967, WITH SCALING=0.95881020276312 | 30 |  | PFref -0.5pu at 5s, -1.5pu at 15s

## CSR_TOV
Deliverable | Category | Figure Number | Clause | Test No | Subtest No | Batch | File_Name | Steps_Per_Write | PSSE | PSCAD | Grid_SCR | Grid_FL_MVA_sig | Grid_X2R_sig | Vpoc_pu_sig | Qpoc_pu | Qpoc_MVAr_sig | Vref_pu_sig | Ppoc_pu | Ppoc_MW_sig | U_Ov | Fault_Time | Fault_Duration | TOV_Timing_Signal_sig | Post_Fault_Duration | Post_Init_Duration_s | TOV_Shunt_C_uF_sig | TOV_MVAr | Column1 | Model_Relpath | PSSE Commands | Vslack_pu_sig | Vpoc_disturbance_pu_sig
CSR | TOV | 1 | 5.5 | 1 |  |  | CSR_5.5_TOV_001_FL2039.54_X2R5.62588_P1_Q-0.427341772151899_V1.077 | 1 | TRUE | TRUE | 8.1582 | 2039.54 | 5.6259 | 1.077 | -0.42734 | -42.2 | 1.0601 | 1 | 250 | 1.1 | 2.5 | 0.1 | 0, AT 2.5s, ↑ 1, AT 2.6s ↓ 0 | 3.8 | 6.4 | 2.7711 | 42.136 | 2.7711 |  | CHANGE FIXED_SHUNT 'tov' MVAR TO 42.1360330276352 AT 2.5s; TRIP FIXED_SHUNT 'tov' AT 2.6s | 1.0821
CSR | TOV | 2 | 5.5 | 2 |  |  | CSR_5.5_TOV_002_FL2039.54_X2R5.62588_P1_Q-0.427341772151899_V1.077 | 1 | TRUE | TRUE | 8.1582 | 2039.54 | 5.6259 | 1.077 | -0.42734 | -42.2 | 1.0601 | 1 | 250 | 1.15 | 2.5 | 0.1 | 0, AT 2.5s, ↑ 1, AT 2.6s ↓ 0 | 3.8 | 6.4 | 8.4313 | 128.2005 | 8.4313 |  | CHANGE FIXED_SHUNT 'tov' MVAR TO 128.20050678135 AT 2.5s; TRIP FIXED_SHUNT 'tov' AT 2.6s | 1.0821
CSR | TOV | 3 | 5.5 | 3 |  |  | CSR_5.5_TOV_003_FL2039.54_X2R5.62588_P1_Q-0.427341772151899_V1.077 | 1 | TRUE | TRUE | 8.1582 | 2039.54 | 5.6259 | 1.077 | -0.42734 | -42.2 | 1.0601 | 1 | 250 | 1.2 | 2.5 | 0.1 | 0, AT 2.5s, ↑ 1, AT 2.6s ↓ 0 | 3.8 | 6.4 | 13.6372 | 207.3576 | 13.6372 |  | CHANGE FIXED_SHUNT 'tov' MVAR TO 207.357595902362 AT 2.5s; TRIP FIXED_SHUNT 'tov' AT 2.6s | 1.0821
CSR | TOV | 4 | 5.5 | 4 |  |  | CSR_5.5_TOV_004_FL2039.54_X2R5.62588_P1_Q-0.427341772151899_V1.077 | 1 | TRUE | TRUE | 8.1582 | 2039.54 | 5.6259 | 1.077 | -0.42734 | -42.2 | 1.0601 | 1 | 250 | 1.25 | 2.5 | 0.1 | 0, AT 2.5s, ↑ 1, AT 2.6s ↓ 0 | 3.8 | 6.4 | 18.4546 | 280.6086 | 18.4546 |  | CHANGE FIXED_SHUNT 'tov' MVAR TO 280.608624447528 AT 2.5s; TRIP FIXED_SHUNT 'tov' AT 2.6s | 1.0821
CSR | TOV | 5 | 5.5 | 5 |  |  | CSR_5.5_TOV_005_FL2039.54_X2R5.62588_P1_Q-0.427341772151899_V1.077 | 1 | TRUE | TRUE | 8.1582 | 2039.54 | 5.6259 | 1.077 | -0.42734 | -42.2 | 1.0601 | 1 | 250 | 1.3 | 2.5 | 0.1 | 0, AT 2.5s, ↑ 1, AT 2.6s ↓ 0 | 3.8 | 6.4 | 22.8972 | 348.1595 | 22.8972 |  | CHANGE FIXED_SHUNT 'tov' MVAR TO 348.159461701775 AT 2.5s; TRIP FIXED_SHUNT 'tov' AT 2.6s | 1.0821
CSR | TOV | 6 | 5.5 | 6 |  |  | CSR_5.5_TOV_006_FL2039.54_X2R5.62588_P1_Q-0.427341772151899_V1.077 | 1 | TRUE | TRUE | 8.1582 | 2039.54 | 5.6259 | 1.077 | -0.42734 | -42.2 | 1.0601 | 1 | 250 | 1.35 | 2.5 | 0.1 | 0, AT 2.5s, ↑ 1, AT 2.6s ↓ 0 | 3.8 | 6.4 | 27.0483 | 411.2779 | 27.0483 |  | CHANGE FIXED_SHUNT 'tov' MVAR TO 411.277943249068 AT 2.5s; TRIP FIXED_SHUNT 'tov' AT 2.6s | 1.0821
CSR | TOV | 7 | 5.5 | 7 |  |  | CSR_5.5_TOV_007_FL2039.54_X2R5.62588_P1_Q-0.427341772151899_V1.077 | 1 | TRUE | TRUE | 8.1582 | 2039.54 | 5.6259 | 1.077 | -0.42734 | -42.2 | 1.0601 | 1 | 250 | 1.4 | 2.5 | 0.1 | 0, AT 2.5s, ↑ 1, AT 2.6s ↓ 0 | 3.8 | 6.4 | 30.9042 | 469.9074 | 30.9042 |  | CHANGE FIXED_SHUNT 'tov' MVAR TO 469.907376407647 AT 2.5s; TRIP FIXED_SHUNT 'tov' AT 2.6s | 1.0821