## Tx Datasheet
Goorambat East 2x 150MVA 220/33kV Transformer
General Transformer Requirements Questions
Voltage Ratios | HV | HV | 220
| LV | LV | 33
Configuration | Vector Group |  | YNd1
Ratings | Continuous | HV | 150
|  | LV | 150
| Overload | HV | NA
|  | LV | NA
Cooling | ODAF | MVA | 150
| ONAN | MVA | TBC by manufacturer
Principal Tap Voltage |  |  | 220
Tapping Range |  |  | +10%/-10% (17 positions, +8,-8 from principal tap)
Tap Size |  |  | 0.0125
Max Tap |  |  | 242kV
Nominal Tap |  |  | 220kV
Min Tap |  |  | 198kV
Impedance at principal tap |  |  | 12% (150 MVA base) +/- 7.5 % of Z% on Principal Tap.
Impedance across tapping range |  |  | TBC by manufacturer
Expected Fault Levels | HV | kA | 40
| LV | kA | 31.5
Earthing Requirements | HV |  | Solidly Earthed
| LV |  | Earthed/ Unearthed/ via an NER (1kA 2 sec)
Physical Config |  |  | Attached Coolers
Noise Enclosures |  |  | None
Blast Walls |  |  | None
Ambient Temperature |  |  | 40 (monthly average - hottest month)
Handrail requirements |  |  | Y
Special Bushing requirements? |  |  | None
Transport Height Restrictions |  |  | As per NW Vic
Transport Weight Restrictions |  |  | As per NW Vic
8 | Load losses at 75°C (load losses determined by wattmeter measurements)
HV to LV at maximum forced cooled rating
8.1 | On principal tapping | kW | 390 (approx)
8.2 | On minimum tapping | kW | 470 (approx)
8.3 | On maximum tapping | kW | 385 (aaprox)
11 | Impedance voltages at 75°C on base of: | MVA
11.1 | HV – LV
| 1. On principal HV Voltage tap | % | 12 (± 7.5% tolerance)
| 2. On principal HV Voltage tap | ohm/phase | 38.72 (Referred to HV)
| 3. On minimum HV Voltage tap | % | 11.8 (± 10% tolerance)
| 3. On minimum HV Voltage tap | ohm/phase | 30.84 (Referred to HV)
| 5. On maximum HV Voltage tap | % | 12.6 (± 10% tolerance)
| 6. On maximum HV Voltage tap | ohm/phase | 49.20 (Referred to HV)
| 7. Maximum impedance over tapping range (including any positive tolerance) | % | 13.86
| 8. Maximum impedance over tapping range (including any positive tolerance) | ohm/phase | 54,11 (Referred to HV)
| 9. Corresponding tap voltage | kV | 242
| 10. Minimum impedance over tapping range (including any negative tolerance) | % | 10.62
| 11. Minimum impedance over tapping range (including any negative tolerance) | ohm/phase | 27.75 (Referred to HV)
| 12. Corresponding tap voltage | kV | 198
12 | Zero sequence impedance on principal tap
12.1 | HV winding with LV O/C | ohm/phase | 34.85 (90% of positive sequence impedance)
12.4 | HV winding with the LV S/C | ohm/phase | 34.85 (90% of positive sequence impedance)
Working
|  | X1 | 0.12
|  | R1 | 0.0026
|  | X0 | 0.108
|  | R0 | 0.00234