## MV Cable Schedule
GOORAMBAT EAST SOLAR FARM
|  | Title |  | MV Cable Schedule
|  | Document Number |  | ENG-GESF-EL-BOQ-6852-D
|  | Revision |  | D1
|  | Date |  | 2024-11-21
Notes:
1) This shall be read in conjunction with the following documents / drawings; ENG-GESF-EL-DWG-6002 and ENG-GESF-EL-DWG-6003 | [10 empty] | `
2) The cable identification label should be secured to both ends of each cable section. This allows the cable section to be identifiable at each asset.
3) Cable lengths have been measured in CAD.
4) 40m has been included for cable ends terminating at the Delivery Substation. 10m per cable end has been included for cables terminating at a PCS. 5% tolerance has been added to the total length.
5) Cable sizes and lengths are provided in advance of the 80% submission and are subject to change.
Cable No. | Feeder Name | From | To | Cable Size (mm2) | Cable Selection | Conductor Type | Insulation | Voltage | Earthing | Length from RMU to RMU | Length per individual phase conductors (x3) | Additional length from RMU to RMU | Additional length per indiidual phase conductors (x3)
1 | PV Feeder 1 | 59 | 1 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 980 | 2940 |  | 0
2 | PV Feeder 1 | 60 | 59 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 259 | 777 |  | 0
3 | PV Feeder 1 | 61 | 60 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 232 | 696 |  | 0
4 | PV Feeder 1 | 62 | 61 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 268 | 804 |  | 0
5 | PV Feeder 1 | 63 | 62 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 249 | 747 |  | 0
6 | PV Feeder 1 | 55 | 63 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 318 | 954 |  | 0
7 | PV Feeder 2 | 67 | 1 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 896 | 2688 |  | 0
8 | PV Feeder 2 | 68 | 67 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 293 | 879 |  | 0
9 | PV Feeder 2 | 69 | 68 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 254 | 762 |  | 0
10 | PV Feeder 2 | 70 | 69 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 364 | 1092 |  | 0
11 | PV Feeder 2 | 71 | 70 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 460 | 1380 |  | 0
12 | PV Feeder 2 | 72 | 71 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 108 | 324 |  | 0
0
13 | PV Feeder 3 | 51 | 1 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 1479 | 4437 |  | 0
14 | PV Feeder 3 | 50 | 51 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 379 | 1137 |  | 0
15 | PV Feeder 3 | 49 | 50 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 499 | 1497 |  | 0
16 | PV Feeder 3 | 48 | 49 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 106 | 318 |  | 0
17 | PV Feeder 3 | 47 | 48 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 230 | 690 |  | 0
18 | PV Feeder 3 | 46 | 47 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 567 | 1701 |  | 0
19 | PV Feeder 4 | 44 | 1 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 1772 | 5316 |  | 0
20 | PV Feeder 4 | 45 | 44 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 276 | 828 |  | 0
21 | PV Feeder 4 | 40 | 45 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 217 | 651 |  | 0
22 | PV Feeder 4 | 43 | 40 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 289 | 867 |  | 0
23 | PV Feeder 4 | 42 | 43 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 306 | 918 |  | 0
24 | PV Feeder 4 | 41 | 42 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 312 | 936 |  | 0
25 | PV Feeder 5 | 39 | 1 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 1813 | 5439 |  | 0
26 | PV Feeder 5 | 38 | 39 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 267 | 801 |  | 0
27 | PV Feeder 5 | 37 | 38 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 246 | 738 |  | 0
28 | PV Feeder 5 | 36 | 37 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 266 | 798 |  | 0
29 | PV Feeder 5 | 35 | 36 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 273 | 819 |  | 0
30 | PV Feeder 5 | 34 | 35 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 234 | 702 |  | 0
31 | PV Feeder 6 | 8 | 1 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 3942 | 11826 | 90 | 270
32 | PV Feeder 6 | 12 | 8 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 194 | 582 |  | 0
33 | PV Feeder 6 | 11 | 12 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 76 | 228 |  | 0
34 | PV Feeder 6 | 14 | 11 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 237 | 711 |  | 0
35 | PV Feeder 6 | 13 | 14 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 121 | 363 |  | 0
36 | PV Feeder 6 | 15 | 13 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 475 | 1425 |  | 0
37 | PV Feeder 7 | 4 | 1 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 4045 | 12135 | 90 | 270
38 | PV Feeder 7 | 2 | 4 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 366 | 1098 |  | 0
39 | PV Feeder 7 | 3 | 2 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 152 | 456 |  | 0
40 | PV Feeder 7 | 1 | 3 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 161 | 483 |  | 0
41 | PV Feeder 7 | 5 | 1 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 381 | 1143 |  | 0
42 | PV Feeder 7 | 6 | 5 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 454 | 1362 |  | 0
43 | PV Feeder 8 | 79 | 2 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 1316 | 3948 |  | 0
44 | PV Feeder 8 | 80 | 79 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 293 | 879 |  | 0
45 | PV Feeder 8 | 76 | 80 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 57 | 171 |  | 0
46 | PV Feeder 8 | 77 | 76 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 467 | 1401 |  | 0
47 | PV Feeder 8 | 82 | 77 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 355 | 1065 |  | 0
48 | PV Feeder 8 | 83 | 82 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 299 | 897 |  | 0
49 | PV Feeder 9 | 81 | 2 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 923 | 2769 |  | 0
50 | PV Feeder 9 | 78 | 81 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 347 | 1041 |  | 0
51 | PV Feeder 9 | 73 | 78 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 97 | 291 |  | 0
52 | PV Feeder 9 | 74 | 73 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 165 | 495 |  | 0
53 | PV Feeder 9 | 75 | 74 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 245 | 735 |  | 0
54 | PV Feeder 10 | 58 | 2 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 853 | 2559 |  | 0
55 | PV Feeder 10 | 57 | 58 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 231 | 693 |  | 0
56 | PV Feeder 10 | 56 | 57 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 242 | 726 |  | 0
57 | PV Feeder 10 | 54 | 56 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 731 | 2193 |  | 0
58 | PV Feeder 10 | 65 | 54 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 74 | 222 |  | 0
59 | PV Feeder 10 | 64 | 65 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 231 | 693 |  | 0
60 | PV Feeder 11 | 52 | 2 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 987 | 2961 |  | 0
61 | PV Feeder 11 | 53 | 52 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 278 | 834 |  | 0
62 | PV Feeder 11 | 33 | 53 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 1255 | 3765 | 90 | 270
63 | PV Feeder 11 | 32 | 33 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 76 | 228 |  | 0
64 | PV Feeder 11 | 20 | 32 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 1540 | 4620 |  | 0
65 | PV Feeder 11 | 16 | 20 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 300 | 900 |  | 0
66 | PV Feeder 12 | 31 | 2 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 1756 | 5268 | 90 | 270
67 | PV Feeder 12 | 30 | 31 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 457 | 1371 |  | 0
68 | PV Feeder 12 | 29 | 30 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 208 | 624 |  | 0
69 | PV Feeder 12 | 28 | 29 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 205 | 615 |  | 0
70 | PV Feeder 12 | 27 | 28 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 229 | 687 |  | 0
71 | PV Feeder 12 | 26 | 27 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 200 | 600 |  | 0
72 | PV Feeder 13 | 66 | 2 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 864 | 2592 |  | 0
73 | PV Feeder 13 | 22 | 66 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 1836 | 5508 | 90 | 270
74 | PV Feeder 13 | 23 | 22 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 209 | 627 |  | 0
75 | PV Feeder 13 | 25 | 23 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 162 | 486 |  | 0
76 | PV Feeder 13 | 24 | 25 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 192 | 576 |  | 0
77 | PV Feeder 13 | 21 | 24 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 280 | 840 |  | 0
78 | PV Feeder 14 | 17 | 2 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 3222 | 9666 | 90 | 270
79 | PV Feeder 14 | 19 | 17 | 630 | 1 | Al | XLPE | 19/33kV | Solid Bond | 406 | 1218 |  | 0
80 | PV Feeder 14 | 18 | 19 | 400 | 1 | Al | XLPE | 19/33kV | Solid Bond | 222 | 666 |  | 0
81 | PV Feeder 14 | 9 | 18 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 441 | 1323 |  | 0
82 | PV Feeder 14 | 10 | 9 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 481 | 1443 |  | 0
83 | PV Feeder 14 | 7 | 10 | 240 | 1 | Al | XLPE | 19/33kV | Solid Bond | 623 | 1869 |  | 0
[11 empty] | 144513 | 540 | 1620 | 1.121%
Switchboard 1 Feeders
Cable Size | Cable Type | Total cable type length
630 | 1c Al XLPE/CWS/HDPE | 19002
400 | 1c Al XLPE/CWS/HDPE | 3606
240 | 1c Al XLPE/CWS/HDPE | 10731
Switchboard 2 Feeders
Cable Size | Cable Type | Total cable type length
630 | 1c Al XLPE/CWS/HDPE | 72147
400 | 1c Al XLPE/CWS/HDPE | 9042
240 | 1c Al XLPE/CWS/HDPE | 29985
Cable Size | Cable Type | Total 3ph feeder length | Total cable length (per conductor)*
630 | 1c Al XLPE/CWS/HDPE | 30383 | 91149
400 | 1c Al XLPE/CWS/HDPE | 4216 | 12648
240 | 1c Al XLPE/CWS/HDPE | 13572 | 40716
*Cable length based on quantity of 1c cables (feeder cable length x3)
Refer to ENG-GESF-EL-DTS-6501 for MV CABLE DATASHEET